## Sheet1
Alarm ID | Tag / Source | Condition | Priority | Operator Message | Recommended Action | Latching | Ack Required
ALM-001 | PT-DISCH-01 | Signal fault / out of range | P2 | Pressure Tx 1 Fault | Check transmitter, cabling; system uses Tx2 if available | Y | Y
ALM-002 | PT-DISCH-02 | Signal fault / out of range | P2 | Pressure Tx 2 Fault | Check transmitter; restore redundancy | Y | Y
ALM-003 | Booster | Both pressure signals invalid | P1 | Pressure Feedback Lost - Control Disabled | Investigate transmitters; switch to manual mode per SOP | Y | Y
ALM-010 | Drive #1 | Drive fault active | P1 | Pump 1 Drive Fault | Review drive fault code; isolate and repair | Y | Y
ALM-011 | Drive #2 | Drive fault active | P1 | Pump 2 Drive Fault | Review drive fault code; isolate and repair | Y | Y
ALM-012 | Drive #3 | Drive fault active | P1 | Pump 3 Drive Fault | Review drive fault code; isolate and repair | Y | Y
ALM-020 | ESD-01 | Emergency stop activated | P1 | Emergency Stop Active | Reset E-stop after ensuring safe conditions | Y | Y
ALM-030 | Booster | Unable to maintain pressure (max pumps running) | P2 | Low Pressure - Capacity Limit | Check demand, leaks, suction conditions | N | Y
ALM-031 | Booster | High discharge pressure | P2 | High Pressure | Check setpoint, valve positions, sensor calibration | N | Y
ALM-040 | Network | Modbus TCP comms loss to any drive | P2 | Drive Communication Lost | Check Ethernet switch, cabling, IP plan | Y | Y