## Sheet1
Option Area | Option | Base/Optional | Design Firm Spec Text (copy/paste hint) | Engineering Notes (SI/Panel Builder)
Enclosure | IP rating (IP54) | Base | Enclosure shall be minimum IP54 floor standing for indoor technical room. | Confirm environment; consider IP55/66 for harsh areas.
Enclosure | Heater + thermostat | Optional | Provide anti-condensation heater where required. | Required for cold/humid sites.
Power quality | Line reactor | Optional | Provide line reactors where required to limit harmonics/protect drives. | Select per drive manufacturer guidance and short-circuit levels.
Power quality | Active/passive harmonic filter | Optional | Harmonic mitigation shall meet utility/end-user limits. | Depends on THDi target and network.
Motor protection | dv/dt filter | Optional | Provide dv/dt filter where long motor cables or motor insulation risk exists. | Determine by cable length and motor type.
Control | Sleep mode (no demand) | Optional | Booster may include sleep mode to stop pumps at no demand. | Tuning required to avoid cycling.
Control | Second pressure transmitter (redundant) | Base | Provide redundant discharge pressure transmitter with automatic fallback. | Implement validation and fallback logic.
Communications | Uplink to SCADA / telemetry | Optional | Provide Ethernet uplink for SCADA/telemetry integration. | Use firewall/DMZ; define protocol (Modbus/OPC).
Cybersecurity | Managed switch + VLAN | Optional | Network shall support segmentation between control and uplink. | Managed switch recommended for VLAN/port security.
Safety | Emergency stop | Project-specific | Emergency stop shall be provided where required by end user. | Define safety category; may require safety relays/STO.