## Parameters
Field | Value
Application | Water Booster Set - 3 Pumps
Starter Type | VSD (Variable Speed Drive)
Motor Power (each) | 30 kW
Quantity | 3 pumps
Redundancy | N+1
Control Mode | Cascade PID
Enclosure | IP54 floor standing
Fieldbus | Modbus TCP (Ethernet)
Cyber Level | IEC 62443 baseline (principles)
Assumed supply | 3~ 400 VAC, 50 Hz (confirm per site)

## I_O_List
Tag | Description | Equipment | Signal Type | Interface | Range / Scaling | Normal | PLC Destination | Alarm? | Notes
PT-DISCH-01 | Discharge pressure transmitter (primary) | Booster | AI | Hardwired | 0-16 bar (example) |  | AI Module Ch1 | Y | Used for PID control
PT-DISCH-02 | Discharge pressure transmitter (redundant) | Booster | AI | Hardwired | 0-16 bar (example) |  | AI Module Ch2 | Y | Auto fallback on fault/out-of-range
ESD-01 | Emergency stop (panel) | Booster Panel | DI | Hardwired |  | Closed | DI Module | Y | Removes run permission
DOOR-SW-01 | Panel door switch | Booster Panel | DI | Hardwired |  | Closed | DI Module | N | Optional (maintenance)
RUNCMD-P1 | Run command Pump 1 | Pump 1 | CMD | Modbus TCP |  |  | Drive #1 Control Word | N | Via network
SPDREF-P1 | Speed reference Pump 1 | Pump 1 | CMD | Modbus TCP | 0-100% |  | Drive #1 Speed Ref | N | Via network (PID output)
STATUS-P1 | Drive status Pump 1 | Pump 1 | FB | Modbus TCP |  |  | Drive #1 Status Word | Y
FAULT-P1 | Drive fault code Pump 1 | Pump 1 | FB | Modbus TCP |  |  | Drive #1 Fault Code | Y
RUNCMD-P2 | Run command Pump 2 | Pump 2 | CMD | Modbus TCP |  |  | Drive #2 Control Word | N | Via network
SPDREF-P2 | Speed reference Pump 2 | Pump 2 | CMD | Modbus TCP | 0-100% |  | Drive #2 Speed Ref | N
STATUS-P2 | Drive status Pump 2 | Pump 2 | FB | Modbus TCP |  |  | Drive #2 Status Word | Y
FAULT-P2 | Drive fault code Pump 2 | Pump 2 | FB | Modbus TCP |  |  | Drive #2 Fault Code | Y
RUNCMD-P3 | Run command Pump 3 | Pump 3 | CMD | Modbus TCP |  |  | Drive #3 Control Word | N | Via network
SPDREF-P3 | Speed reference Pump 3 | Pump 3 | CMD | Modbus TCP | 0-100% |  | Drive #3 Speed Ref | N
STATUS-P3 | Drive status Pump 3 | Pump 3 | FB | Modbus TCP |  |  | Drive #3 Status Word | Y
FAULT-P3 | Drive fault code Pump 3 | Pump 3 | FB | Modbus TCP |  |  | Drive #3 Fault Code | Y

## Alarm_List
Alarm ID | Tag / Source | Condition | Priority | Operator Message | Recommended Action | Latching | Ack Required
ALM-001 | PT-DISCH-01 | Signal fault / out of range | P2 | Pressure Tx 1 Fault | Check transmitter, cabling; system uses Tx2 if available | Y | Y
ALM-002 | PT-DISCH-02 | Signal fault / out of range | P2 | Pressure Tx 2 Fault | Check transmitter; restore redundancy | Y | Y
ALM-003 | Booster | Both pressure signals invalid | P1 | Pressure Feedback Lost - Control Disabled | Investigate transmitters; switch to manual mode per SOP | Y | Y
ALM-010 | Drive #1 | Drive fault active | P1 | Pump 1 Drive Fault | Review drive fault code; isolate and repair | Y | Y
ALM-011 | Drive #2 | Drive fault active | P1 | Pump 2 Drive Fault | Review drive fault code; isolate and repair | Y | Y
ALM-012 | Drive #3 | Drive fault active | P1 | Pump 3 Drive Fault | Review drive fault code; isolate and repair | Y | Y
ALM-020 | ESD-01 | Emergency stop activated | P1 | Emergency Stop Active | Reset E-stop after ensuring safe conditions | Y | Y
ALM-030 | Booster | Unable to maintain pressure (max pumps running) | P2 | Low Pressure - Capacity Limit | Check demand, leaks, suction conditions | N | Y
ALM-031 | Booster | High discharge pressure | P2 | High Pressure | Check setpoint, valve positions, sensor calibration | N | Y
ALM-040 | Network | Modbus TCP comms loss to any drive | P2 | Drive Communication Lost | Check Ethernet switch, cabling, IP plan | Y | Y

## BOM_Template
Category | Item | Qty | Schneider Family (example) | Part No. | Key Selection Notes / Options
Enclosure | Floor standing enclosure IP54 (with plinth, gland plate) | 1 | Spacial / Universal enclosure family | TBD | Size to be confirmed by panel builder based on heat dissipation and layout
Power Incomer | Main isolator and MCCB | 1 | Compact NSX / equivalent | TBD | Size to site fault level and max current; include lockable handle
Drive Feeder | VSD 30 kW (x3) | 3 | Altivar Process / general purpose VSD | TBD | Confirm supply voltage, overload class, EMC category
Drive Options | Line reactor (optional) per drive | 3 | Line reactor | TBD | As required for harmonics / protection
Drive Options | dv/dt filter (optional) per drive | 3 | Output filter | TBD | As required for long motor cables
Control | PLC CPU + Ethernet | 1 | Modicon PLC family | TBD | Must support Modbus TCP client/master and required I/O
Control | Analog input module (pressure) | 1 | Analog input module | TBD | 2 x AI (4-20 mA) minimum
Control | Digital input module (E-stop, door, permissives) | 1 | Digital input module | TBD | Size per project
HMI | Local operator terminal | 1 | EcoStruxure Operator Terminal | TBD | Basic status, commands, alarms, trends
Networking | Industrial Ethernet switch | 1 | ConneXium / industrial switch family | TBD | Ports >= 6; managed switch preferred if segmentation required
Power Supply | 24 VDC power supply | 1 | Phaseo / PSU family | TBD | Size to PLC+HMI+switch+instrument loops
Signaling | Panel indicators, buzzer (optional) | 1 | Harmony signaling | TBD | Per end user preference
Safety | Emergency stop button (if required) | 1 | Harmony E-stop | TBD | Remove run permissive; local regulation applies
Documentation | Drawings, programs, FAT/SAT forms | 1 | N/A | N/A | Deliverables as per spec appendix

## Network_IP_Plan
Device | Role | Protocol | IP Address (example) | Subnet | VLAN/Zone | Notes
PLC | Controller | Modbus TCP client | 192.168.10.10 | 255.255.255.0 | Control Panel Zone | Static IP
HMI | Operator interface | HMI/SCADA | 192.168.10.20 | 255.255.255.0 | Control Panel Zone | Static IP
Ethernet Switch | Network infrastructure | N/A | 192.168.10.2 | 255.255.255.0 | Control Panel Zone | Managed switch preferred
VSD #1 | Drive Pump 1 | Modbus TCP server | 192.168.10.31 | 255.255.255.0 | Control Panel Zone | Static IP
VSD #2 | Drive Pump 2 | Modbus TCP server | 192.168.10.32 | 255.255.255.0 | Control Panel Zone | Static IP
VSD #3 | Drive Pump 3 | Modbus TCP server | 192.168.10.33 | 255.255.255.0 | Control Panel Zone | Static IP
Uplink to SCADA (optional) | Operations network | Modbus/OPC | 192.168.20.10 | 255.255.255.0 | Operations Zone | Via firewall/DMZ where required

## Option_Matrix
Option Area | Option | Base/Optional | Design Firm Spec Text (copy/paste hint) | Engineering Notes (SI/Panel Builder)
Enclosure | IP rating (IP54) | Base | Enclosure shall be minimum IP54 floor standing for indoor technical room. | Confirm environment; consider IP55/66 for harsh areas.
Enclosure | Heater + thermostat | Optional | Provide anti-condensation heater where required. | Required for cold/humid sites.
Power quality | Line reactor | Optional | Provide line reactors where required to limit harmonics/protect drives. | Select per drive manufacturer guidance and short-circuit levels.
Power quality | Active/passive harmonic filter | Optional | Harmonic mitigation shall meet utility/end-user limits. | Depends on THDi target and network.
Motor protection | dv/dt filter | Optional | Provide dv/dt filter where long motor cables or motor insulation risk exists. | Determine by cable length and motor type.
Control | Sleep mode (no demand) | Optional | Booster may include sleep mode to stop pumps at no demand. | Tuning required to avoid cycling.
Control | Second pressure transmitter (redundant) | Base | Provide redundant discharge pressure transmitter with automatic fallback. | Implement validation and fallback logic.
Communications | Uplink to SCADA / telemetry | Optional | Provide Ethernet uplink for SCADA/telemetry integration. | Use firewall/DMZ; define protocol (Modbus/OPC).
Cybersecurity | Managed switch + VLAN | Optional | Network shall support segmentation between control and uplink. | Managed switch recommended for VLAN/port security.
Safety | Emergency stop | Project-specific | Emergency stop shall be provided where required by end user. | Define safety category; may require safety relays/STO.