Application Specification Appendix
Water Booster Set - 3 Pumps (N+1)

VSD Control Panel - 3 x 30 kW | IP54 Floor Standing | Cascade PID | Modbus TCP | IEC 62443 Baseline

Version: v1.0  |  Date: 2026-02-27

# 1. Purpose and How to Use

This document is a copy/paste-ready specification appendix intended for Design Firms to include in Concept/FEED and Basic Design packages. It defines a repeatable solution approach for a water booster application and enables early-stage prescription of the complete motor control solution (enclosures, protection, variable speed drives, control, communications, and testing).

This appendix is technology- and outcome-oriented, but references Schneider Electric solution families where applicable. Final product references (exact part numbers) shall be confirmed during detailed design by the System Integrator / Panel Builder according to local catalog, short-circuit levels, environmental conditions, and end-user standards.

# 2. Application Data Sheet

| Application | Water Booster Set - 3 Pumps |
| --- | --- |
| Process objective | Maintain discharge pressure at setpoint across variable demand |
| Motor configuration | 3 pumps x 30 kW each; redundancy N+1 (one pump available as standby) |
| Starter type | Variable Speed Drive (VSD) for each pump |
| Control mode | Cascade PID with staging/de-staging and automatic alternation |
| Enclosure | IP54 floor standing control panel (universal enclosure) |
| Communications | Modbus TCP (Ethernet) between PLC and drives; optional uplink to SCADA |
| Cybersecurity | Baseline requirements aligned with IEC 62443 principles (zones, accounts, logging) |

# 3. Reference Architecture

The reference architecture below provides a typical power and control arrangement for a 3-pump booster set with VSD control. It is intended as an early-stage template. The detailed GA, heat dissipation, cable entry, and assembly details shall be provided by the selected panel builder.

Figure 1 - Reference architecture (power + controls + Modbus TCP).

Figure 2 - Typical single line diagram (concept).

# 4. Panel Scope and Deliverables

The booster control panel assembly shall include, as a minimum:

Main incoming isolator and/or MCCB sized for the panel maximum demand and fault level.

Three (3) VSD feeders sized for 30 kW motors, including appropriate upstream protection and isolation as per applicable standards.

PLC with sufficient Ethernet capability and I/O for pressure feedback, permissives, local controls, and alarms.

Local operator interface (HMI) and basic local controls (e.g., Auto/Off/Hand selector, Reset, Emergency stop where required).

Industrial Ethernet switch for Modbus TCP network connectivity (drives + PLC + HMI).

Panel auxiliaries: 24 VDC power supply, control protection, terminal blocks, labeling, earthing, and service accessories (lighting/heater as required).

Documentation set: electrical drawings, I/O list, network IP plan, PLC/HMI backups, FAT/SAT records.

# 5. Electrical Requirements (Copy/Paste Spec Clauses)

5.1 Enclosure and Assembly

The control panel enclosure shall be floor standing with minimum ingress protection rating IP54 and suitable for indoor technical room installation unless stated otherwise.

The enclosure shall include a gland plate (or equivalent) for bottom cable entry, earthing bar, and provision for safe maintenance access.

The panel builder shall provide thermal management (fan/filter or air conditioning as required) to maintain component temperatures within manufacturer limits at site ambient conditions.

All components shall be clearly labeled; wiring shall be ferruled and identified in accordance with the drawings.

The assembly shall be designed, manufactured, and tested in accordance with applicable IEC requirements for low-voltage switchgear and controlgear assemblies (e.g., IEC 61439 where applicable).

5.2 VSD Feeders

Each pump motor shall be controlled by an individual VSD suitable for 30 kW motor duty and the supply network characteristics (voltage, frequency, short-circuit level).

The VSD shall support network control and monitoring via Modbus TCP and shall expose key operating data (run status, speed reference, current, power, energy, and fault codes).

The design shall include appropriate upstream protection and isolation for each VSD feeder; additional line/reactor or harmonic mitigation devices shall be included where required by grid code, EMC, or harmonic limits.

Motor cable length limits and output filtering (e.g., dv/dt filter) shall be addressed during detailed design based on site layout.

5.3 Control Power and Auxiliaries

The panel shall include a 24 VDC control power supply sized for PLC, HMI, network devices, and field instrumentation loops as required.

An emergency stop function (if specified by the end user) shall remove run permission from all drives and place the system into a safe state.

Door interlock and maintenance mode provisions shall be implemented as required by local regulations and end user standards.

# 6. Control Philosophy - Cascade PID (Booster Set)

The booster set shall maintain discharge pressure at a configurable setpoint using cascade PID control and automatic staging of pumps. The PLC shall coordinate drive start/stop and speed references over Modbus TCP.

Minimum functional requirements:

PID pressure control using a primary discharge pressure transmitter; automatic fallback to redundant transmitter upon fault/out-of-range.

Pump staging: start Lead pump on demand; add Lag pumps when pressure cannot be maintained (e.g., Lead speed above high threshold for a time delay).

Pump de-staging: stop Lag pumps when demand decreases (e.g., average speed below low threshold for a time delay) while maintaining stable pressure control.

Automatic alternation of Lead/Lag duty to equalize runtime and support N+1 redundancy (one pump available as standby).

Anti-short-cycle logic: minimum run time and minimum stop time per pump.

Sleep mode (optional): if no demand (stable pressure at low speed limit) the system may stop all pumps and restart on pressure drop.

Permissives and interlocks: suction pressure permissive (if provided), valve position permissives (if provided), local emergency stop, drive healthy status.

Failover: if any pump/drive becomes unavailable, remaining pumps shall continue to control pressure subject to capacity.

# 7. Communications - Modbus TCP

The PLC shall act as Modbus TCP client/master. Each VSD shall be a Modbus TCP server. The network shall be designed for deterministic control, with segregation from corporate networks.

Each drive shall have a unique IP address; an IP plan shall be delivered as part of the documentation set.

Minimum data exchanged per drive: start/stop, speed reference, control mode, run feedback, speed feedback, current, power, energy, fault status, and fault code.

Loss of communications shall generate an alarm and drive/run commands shall fail to a defined safe state (configurable).

# 8. Cybersecurity Baseline (IEC 62443-aligned)

This project shall implement baseline cybersecurity controls consistent with IEC 62443 principles. These requirements are written to be achievable for typical water booster deployments while improving security by design.

Define zones and conduits: (1) Booster Control Panel zone (PLC, drives, HMI, switch); (2) Site Operations zone (SCADA/operations); (3) Corporate zone.

Unique user accounts on PLC/HMI where supported; role-based access; default passwords shall be changed at commissioning.

Network segmentation: booster control network shall be separated from corporate networks (VLAN/firewall/industrial DMZ where applicable).

Disable unused services and ports; maintain an inventory of firmware/software versions.

Event logging: security-relevant events (login attempts, configuration changes, comms loss) shall be logged and available for export.

Remote access (if required) shall use secure methods with MFA and audit trail; no direct inbound access to control network from the internet.

# 9. FAT/SAT - Minimum Acceptance Tests

Factory Acceptance Test (FAT) - minimum scope:

Visual inspection: wiring, labeling, earthing, component installation, enclosure integrity.

Electrical tests: continuity, insulation, protective earth verification (per applicable standards).

Network tests: verify Modbus TCP communications to each VSD; validate data exchange list.

Functional tests (simulation where necessary): pump staging/de-staging, alternation, permissives, alarms, fallback to redundant pressure transmitter.

HMI tests: start/stop, setpoint entry, alarm acknowledgement, runtime counters, status screens.

Site Acceptance Test (SAT) - minimum scope:

Verify field wiring termination and correct motor rotation.

Verify pressure transmitter calibration and signal scaling.

Prove PID stability and staging thresholds under representative demand conditions.

Prove redundancy behavior (simulate one pump/drive unavailable).

Confirm alarm annunciation to local HMI and (if applicable) SCADA.

# Appendix A - Asset Pack Contents

This appendix is intended to be used with the following asset files:

SpecTextBlocks.txt - copy/paste clauses for tenders

ApplicationPack.xlsx - I/O list, alarm list, BOM template, network IP plan

01_Reference_Architecture.pdf/.png - reference architecture figure

02_Single_Line_Diagram.pdf/.png - single line figure